Model 8011 Commercial Corner Ultimate RiserPACK

  - SPRINKLER SPECIALTY PIPE FITTINGS - Flow Detection and Test Assemblies:

Product: Commercial Model 8011. Includes a flow switch, TESTanDRAIN Model 1011A, Model 7600 3-way Globe Valve, and a 7500 Pressure Gauge and a model 7000L Pressure Relief Valve.

Riser Assembly: Pre-Assembled TESTanDRAIN Riser: 2, 2-1/2, 3, 4, 6, and 8 inches (51 mm, 64 mm, 76 mm, 102 mm, 152 mm, 203 mm):

Inlet and outlet (Schedule 10 steel): Grooved ends per AWWA C606

Fabricated Schedule 10 steel body with minimum 3 mil (.08 mm) red powder-coated finish

Listings: UL listed and FM approved; compliant with NFPA 13

Pressure Rating:  300 psig (2070 kPa).

Size:  Same as connected piping.

** NOTE TO SPECIFIER **  Delete valve  not required.

Valve Model 1011 TESTanDRAIN valve for a 2 inch (51 mm) Model:

1 inch (25 mm) FNPT.

** NOTE TO SPECIFIER **  Delete orifice size not required.

Test Orifice Size:  Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition

Valve Model 1011 TESTanDRAIN valve for a 2-1/2 or 3 inch (64 mm, 76 mm) Models:

1-1/4 inch FNPT.

** NOTE TO SPECIFIER **  Delete orifice size not required.

        - Test Orifice Size:  Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition.

- Test Orifice Size:  Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.

Valve Model 1011 TESTanDRAIN valve for a 4, 6, or 8 inch (102 mm, 152 mm, 203 mm) Models:

2 inch FNPT.

** NOTE TO SPECIFIER **  Delete orifice size not required.

Test Orifice Size:  Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 25.2K, as required by NFPA 13, latest edition.

Water flow alarm switch.

Pressure Gauge:  AGF Model 7500.

1/4 inch, 3-way globe valve:  AGF Model 7600

Pressure Relief Valve and Drainage Piping:  AGF Model 7000L

** NOTE TO SPECIFIER **  Delete pressure rating not required.

Pressure Rating:  Factory rated at 175 PSI.

Pressure Rating:  200 PSI.

Pressure Rating:  225 PSI.

Pressure Rating:  300 PSI.

Body Material:  Bronze body and stainless steel spring.

Components:  Nylobraid flexible tube, Two 1/2 inch (13 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris.

1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.

Relief pressure shall be factory set to project specifications.

Relief valve shall operate to the OPEN position between 90% and 105% of the set pressure.

Relief valve shall reseat or CLOSE at a minimum of 80% of set pressure.

Optional System Control Valve (Butterfly) Grooved Butterfly Valve with
          Tamper Switch (Normally Open):

- ** NOTE TO SPECIFIER ** Delete if not required.

Sizes: 2" through 8"
b.       Grooved ends conforming to AWWA C606
c.       Designed for fire protection service
d.       Includes supervisory tamper switch with weatherproof actuator
e.       Pressure Rating: 300 psi
f.        Temperature Range: 32°F to 175°F
g.       Listings: UL/ULC listed and FM approved
h.       Coating: Fusion bonded epoxy coating

Optional Check Valve (System Control Valve) Grooved Resilient Swing Check Valve ** NOTE TO SPECIFIER ** Delete if not required.

Sizes: 2" through 8"

Grooved ends conforming to AWWA C606

Pressure Rating: 300 psi

Temperature Range: 32°F to 175°F

Listings: UL/ULC listed and FM approved

Body: ASTM A536 ductile iron

Seat: EPDM resilient sealing

Coating: Fusion bonded epoxy coating

Optional Flexible Main Drain Connection

** NOTE TO SPECIFIER ** Delete if not required.

a. 	Flexible drain hose assembly connected to main drain outlet
b. 	Minimum 1 inch (25 mm) internal diameter unless otherwise specified
c. 	Hose material: Reinforced braided flexible tubing rated for system pressure
d. 	Includes threaded or barbed fittings for connection to drain piping
e. 	Designed to allow simplified routing to floor drain without rigid piping alignment