- Model 7200L/ Pressure Relief Valves

- 2.1	PRESSURE RELIEF VALVES

Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing, Inc.; Model [7200L]

<Insert manufacturer's name>.

Standard:  UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.  NFPA 13, 13R, 13D (as applicable).

Pressure Rating: Factory rated at 175 PSI. [200 PSI] [225 PSI] [300 PSI].

Body Material: Bronze body and stainless steel spring

Components: External identification plate, integral flushing handle to remove debris, and lockout feature to isolate valve from the system for hydrostatic testing

¾ inch MIPT inlet, ¾ inch FIPT outlet

Relief pressure shall be factory set to project specifications

Relief valve shall operate to the OPEN position between 90% and 105% of the set pressure

Relief valve shall reseat or CLOSE at a minimum of 80% of set pressure.