Model 2500 TESTanDRAIN

- 2.1	SPRINKLER SPECIALTY PIPE FITTINGS

Flow Detection and Test Assemblies:

Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing Inc.; Model 2500 TESTanDRAIN.

<Insert manufacturer's name>.

Standard:  UL's "Product iQ" listing or "Approval Guide," published by FM Global, listing.  NFPA 13, 13R, 13D (as applicable).

Pressure Rating:  300 psig (2070 kPa).

Materials:  Bronze body, brass stem, impregnated Teflon seat, chrome coated brass ball, and a steel handle with positive stops at the TEST and DRAIN positions

Components:  A tamper resistant test orifice, integral tamper resistant sight glasses, a tapped and plugged port for system access, and a steel identification plate.

Test Orifice Size: Nominal [2.8K (3/8 inch), 4.2K (7/16 inch), 5.6K (1/2 inch), 8.0K (17/32) inch, 11.2K (5/8 inch, ELO), 14.0K (3/4 inch, ESFR), K25.2], as required by NFPA 13, latest edition.

Inlet and Outlet Size:  [1 inch NPT] [1-1/4 inch NPT] [1 inch Groove] [1-1/4 inch Groove] [2 inch Groove].

Options:

Bypass drain port in the valve body for use with a pressure relief valve and associated drainage piping.

Locking Plate Kit: Provides vandal resistance and prevents accidental alarm activation by locking the valve handle in the “OFF” position.

Locking Plate: Carbon steel.

Lock: 1-1/2 inch wide solid brass with a 3/8 inch chrome plated hardened steel shackle.

For use with a [3/4 inch] [1 inch] [1-1/4 inch] [1-1/2 inch] [2 inch] valve.