Model 8611 Commercial Corner RiserPACK

  - SPRINKLER SPECIALTY PIPE FITTINGS - Flow Detection and Test Assemblies:

Product:  Commercial Model M8611. Includes a flow switch, TESTanDRAIN Model 1011A, Model 7600 3-way Globe Valve, and a M7500 Pressure Gauge and a model M7000L Pressure Relief Valve.

Riser Model:  Pre-Assembled TESTanDRAIN Riser 2, 2-1/2, 3, 4, 6, and 8 inches (51mm, 64 mm, 76 mm, 102 mm, 152 mm, 203 mm):

Inlet and Outlet (Schedule 10 steel): Grooved 2, 2-1/2, 3, 4, 6, and 8 inches (51mm, 64 mm, 76 mm, 102 mm, 152 mm, 203 mm) Models.

Schedule 10 fabricated steel body with 3mil (.08 mm) powder coated red finish.

Standard:  UL's "Product iQ" listing, or "Approval Guide," published by FM Global, listing.  NFPA 13.

Pressure Rating:  300 psig (2070 kPa).

Size:  Same as connected piping.

** NOTE TO SPECIFIER **  Delete valve  not required.

Valve Model 1011 TESTanDRAIN valve for a 2 inch (51 mm) Model:

1 inch (25 mm) FNPT.

** NOTE TO SPECIFIER **  Delete orifice size not required.

Test Orifice Size:  Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition

Valve Model 1011 TESTanDRAIN valve for a 2-1/2 or 3 inch (64 mm, 76 mm) Models:

1-1/4 inch FNPT.

** NOTE TO SPECIFIER **  Delete orifice size not required.

        - Test Orifice Size:  Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition.

        - Test Orifice Size:  Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.

Valve Model 1011 TESTanDRAIN valve for a 4 or 6 inch (102 mm, 152 mm) Models:

2 inch FNPT.

** NOTE TO SPECIFIER **  Delete orifice size not required.

Test Orifice Size:  Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 14.0K (3/4 inch, ESFR), as required by NFPA 13, latest edition.

Test Orifice Size:  Nominal 25.2K, as required by NFPA 13, latest edition.

Water flow alarm switch.

Pressure Gauge:  AGF Model 7500.

1/4 inch, 3-way globe valve:  AGF Model 7600

Pressure Relief Valve and Drainage Piping:  AGF Model 7000L

** NOTE TO SPECIFIER **  Delete pressure rating not required.

Pressure Rating:  Factory rated at 175 PSI.

Pressure Rating:  200 PSI.

Pressure Rating:  225 PSI.

Pressure Rating:  300 PSI.

Body Material:  Bronze body and stainless steel spring.

Components:  Nylobraid flexible tube, Two 1/2 inch (13 mm) NPT by barbed 90 degree elbows, external identification plate and integral flushing handle to remove debris.

1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.

Relief pressure shall be factory set to project specifications.

Relief valve shall operate to the OPEN position between 90% and 105% of the set pressure.

Relief valve shall reseat or CLOSE at a minimum of 80% of set pressure.