Model 5200A COLLECTanDRAIN

- 2.1	SPRINKLER SPECIALTY PIPE FITTINGS

Auxiliary Drain and Condensation Collecting Assemblies for Dry Pipe and Preaction Sprinkler Systems:

Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing Inc.; Model 5200A COLLECTanDRAIN™.

<Insert manufacturer's name>.

Standards:

NFPA 13 and NFPA 25.

Material:

Galvanized Auxiliary Drain with Anti-Trip Plate.

Black Steel Pipe Auxiliary Drain with Anti-Trip Plate

Components:

Two1 inch (13 mm)  MIPT x FIPT Brass quarter turn ball valves with chrome plated balls.

Anti-Trip Plate (ATP): Prevents the opening of either the upper or lower drain valve unless the opposite valve is in the correct closed position, preventing an accidental/malicious tripping of the alarm valve and filling of the sprinkler system.

ATP is powder coated safety red for corrosion resistance and silk-screened with both “AUXILIARY DRAIN” and operating instructions.

ATP can be locked to prevent tampering.

Anti-Trip Plate Mounting Hardware Set.

Two 1 inch by 2 inch (25 mm by 51 mm) Bell Reducers.

2 inch by 12 inch (51 mm by 305 mm)  Condensate Nipple.

1 inch (15 mm) Galvanized Square Head Plug.